Timeline released by the city of Frederick, Md.:

Sunday, December 11, 2011

- 5:30 pm – Waste Water Treatment Plant lost utility power

  - NOTE: The plant has three emergency generators that are tested weekly. When utility power is lost, there are controls that start the generators automatically. When this loss of power happened the generators tried to start as controlled. The operator on duty found the generators to be having issues running correctly and as mandated in a Department of Public Works (DPW) Standard Operating Procedures (SOP) called the City Maintenance superintendent.

- 5:50 pm – The operator called the Jason Michael, Superintendent Facilities Maintenance

- 6:05 pm - Jason Michael, Superintendent of Facilities Maintenance, came and started the generators but was unable to switch the plant load to them. He went directly to the control substation and found the visible damage that was fatal to the system. Calls went out immediately to Allegheny power to come on site and stop the power feed so the equipment could be opened and investigated without someone losing their life.

- 6:10 pm– Stona Cosner, Superintendent of Wastewater, was called and headed into the plant

- 6:15 pm – Jason Michael, Superintendent Facilities Maintenance, called Chip Stitley, Superintendent of Sewer Maintenance, to advise of the potential for a backup in the collection system and requested response from his department

- 6:19 pm – Jason Michael called Marc Stachowski, Deputy Director of Public Works, to advise him of the situation

- 6:35 pm – Marc Stachowski notified Mayor Randy McClement

- 7:00 pm -The wastewater flow that would normally enter the treatment plant backed up because of the power outage and forcibly pushed the main influent manhole off on its own. Stona Cosner and DPW staff moved them out of the way and barricaded the area for safety. No other manholes were removed by staff.

- 7:44 pm– Stona Cosner called Susan Harding, Public Information Officer (PIO), to alert the public via press release, Nixle, Facebook, Twitter

- 7:50 pm – Stona Cosner called MDE to report the bypass

- 8:30 pm– Potomac Edison made it safe for DPW staff to open the utility and generator switchgear equipment. Again, for DPW staff to handle this medium voltage equipment without personal injury or loss of life we had to make it safe.

- 9:00 pm– Staff completed an initial inspection of the equipment to assess the damage and found signs of an underground cable fault that caused water and carbon debris all through the switch gear and control equipment. The cause is still under investigation.

  - Note - From 9:00 pm on 12.11.11 to approx. 3:00 am on 12.12.11 – The switch gear and control equipment had to be disassembled, cleaned and tested before starting the generators because again, personnel safety and equipment safety had to be confirmed.

- Susan Harding, PIO, received the first call from Stona Cosner at 7:44 PM on 12.11.11 requesting the issuance of a press release and to call the County Health Department. The PIO was on the highway enroute home and called Josh Russin, Executive Assistance to the Mayor, to see if he could contact Dr. Brookmyer which was the first he was informed of the incident.

- Susan Harding received a second call from Keith Brown at 8:16 pm with the same information. Susan Harding called Dr. Brookmyer and left a message.

- At 8:38 pm, Dr. Brookmyer sent Susan Harding an email stating that she had received Susan’s message as well as a call from Josh Russin.

- At 8:45pm Susan Harding sent the initial press release out

- At approx. 8:47 pm an alert went up on the website, the press release went up on the website, Facebook, Twitter and was sent via Nixle (the City’s online alert notification system).

- In trying to initially reach Dr. Brookmyer, Susan Harding called the off hours/emergency numbers the Frederick County Health Department. Susan Harding reached the staff on call for the Maryland Department of the Environment (MDE), which is covered by the Maryland Emergency Management Agency (MEMA) on the weekends. He said he would communicate to the proper channels.

- At approximately 11:00 pm, Susan Harding received a call from Mr. George Keller, Frederick County Health Department (FCHD) Director of Environmental Health. He offered any support and said he had been in touch with City DPW. He stated that he spoke to Stona Cosner earlier that evening.

- At 11:18 pm, Susan Harding, PIO sent the following to Mayor McClement, Marc Stachowski, Jason Michael, Josh Russin, Keith Brown, and Eva Cosner regarding my conversation with Mr. Keller:

- Mr. Keller has given me one additional sentence to put into my next press release “Frederick County Health Department cautions citizens to avoid water contact downstream of the point of overflow which is at Carroll Creek and the Monocacy River on Gas House Pike.”

- Mr. Keller will call Stona when the City enters the recovery mode and ask that water samples be taken upstream and downstream over a period of time from the point of the overflow – this is for comparison

- Mr. Keller notified the MDE Duty Officer

- MDE and Frederick County offers assistance in any way even if it is for moral support

- Mr. Keller’s cell phone number is 240.405.2293

Monday, December 12, 2011

- At approximately 3:30 am on 12.12.11, Susan Harding, PIO, received a call from Dispatch and was asked to send out a press release stating that the WWTP was on generator power and GAS House Pike was open for traffic. A press release went out at 4:01 AM, (on website, Nixle, Twitter, & Facebook)

- At 4:58 am, after getting all processes running, Stona Cosner called MDE back to report the bypass had stopped at 3:00 am 12/12/11.

- 9:00 am, Stona Cosner had operators clean up any debris from the spill for disposal and spread 200 lbs. of lime over the area.

- At 10:56 am, Susan Harding sent an update press release to Dr. Brookmyer, Mayor McClement and Marc Stachowski outlining the issue using information received from Marc Stachowski and asked for additional information and review of content.

- At 11:34 am, Susan Harding received the following email from Dr. Brookmyer

Susan –

Thank you for your call asking if there was any additional content or additional public notifications needed from the local health department perspective. You have done a good job covering the critical information. Since there are no actions for the public to take other than the simple message to avoid contact with water along the route (it would be good to provide updated information as to how far the contamination is present so people will have better information about the location above which should be avoided). MDE usually requires that the waterways be posted until testing determines that background [contamination] levels have been achieved. I forgot to ask you if that has been done already. Extra signage is usually posted near parks and other areas where people take their pets and children.

My staff are following-up with MDE to confirm that MDE will be preparing or perhaps already issued a press release regarding information relevant any contamination that may be present outside of Frederick County’s boundaries. – Barbara

Barbara A. Brookmyer, MD, MPH

Health Officer

Frederick County Health Department

350 Montevue Lane

Frederick, Maryland 21702

Tel: 301-600-2509

Fax: 301-600-3111

E-mail: < BBrookmyer@FrederickCountyMD.gov>

- On 12.12.2011 at 2:12 pm – Marc Stachowski sent an email to Mr. Keller asking for direction regarding sampling.

- On 12.13.2011 – Stone Cosner also left a voice mail for Mr. Keller

- On 12.14.2011 – Mr. Keller returned Stona’s call ( Mr. Keller was on leave 12.13.11)

- On 12.14.2011 – Marc Stachowski sent Mr. Keller an email stating that Dan Seal, Supervisor of Water Quality, will be taking water samples until further notice. Mr. Stachowski will keep Mr. Keller updated.